## Distribution panel 1
|  | Efficiency | 0.8 |  | CYBERNETIK
|  | Power Factor | 0.8 |  | Total KW | 144.9875
|  | Line to Line Voltage | 415 |  | Total HP | 194.3532
|  | Single Phase voltage | 120 |  | Total Amp | 252.4331
|  | KW to HP Conversion | 0.746 |  | Design Total KW | 178.3346
|  | Design Factor | 1.23 |  | Design Total HP | 239.0545
|  | KVA to KW Conversion | 0.8 |  | Design Total Amp | 310.4928
CYBERNETIK MACHINE
Zone | Sr. No | Device | Name | DOL/VFD/Thyrister | KW | Total (KW) | HP | Amp
System | 1 | Chopper Panel | CP01 | MCCB | 14.7875 | 14.7875 | 19.8224 | 37.4781
| 2 | Chopper Panel feeder-1 | CPF01 | MCCB | 29 | 29 | 38.874 | 63.0408
| 3 | Chopper Panel feeder-2 | CPF02 | MCCB | 29 | 29 | 38.874 | 63.0408
| 4 | Dryer panel | DRP01 | MCCB | 51.8 | 51.8 | 69.437 | 117.1086
| 5 | Packing panel | PKP01 | MCCB | 20 | 20 | 26.8097 | 49.6898
| Total |  |  |  | 144.5875 | 144.5875 | 193.817 | 330.3582
Transformer Load
| Sr. No | Device | Name | KVA | KW | Total (KW) | HP | P Amp
Control | 1 | Transformer-1 (230VAC) | TR-1 | 0.5 | 0.4 | 0.4 | 0.53619 | 0.69562
(Utility)
| Total |  |  |  | 0.4 | 0.4 | 0.53619 | 0.69562
Total Connected |  |  |  |  | 144.9875 | 144.9875 | 194.3532 | 331.0538
Total Designed(1.23) |  |  |  |  | 178.3346 | 178.3346 | 239.0545 | 407.1962

## Chopper Zone Load
|  | Efficiency | 0.8 |  | CYBERNETIK
|  | Power Factor | 0.8 |  | Total KW | 11.83
|  | Line to Line Voltage | 415 |  | Total HP | 15.8579
|  | Single Phase voltage | 230 |  | Total Amp | 20.5968
|  | KW to HP Conversion | 0.746 |  | Design Total KW | 14.7875
|  | Design Factor | 1.25 |  | Design Total HP | 19.8224
|  | KVA to KW Conversion | 0.8 |  | Design Total Amp | 25.746
CYBERNETIK MACHINE
Zone | Sr. No | Device | Name | DOL/VFD/Thyrister | KW | Total (KW) | HP | Amp | Drive amp | Motor KW
System | 1 | Chopper Motor-1 | CM001 | VFD | 4 | 4 | 5.3619 | 8.6953 | 10.5 | 3.7
| 2 | Chopper Motor-2 | CM002 | VFD | 4 | 4 | 5.3619 | 8.6953 | 10.5 | 3.7
| 3 | Anti-Static Coating Roller | ASCR001 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.5
| 4 | Spreader Motor-2 | SM001 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.5
| 5 | Feeders-1 (In Future Scope with DOL) | - | DOL | 0.18 | 0.18 | 0.24129 | 0.39129 | 0.4 | 0.18
| 6 | Feeders-2 (In Future Scope with DOL) | - | DOL | 0.18 | 0.18 | 0.24129 | 0.39129 | 0.4 | 0.18
| 7 | Feeders-3 (In Future Scope with DOL) | - | DOL | 0.37 | 0.37 | 0.49598 | 0.80431 | 0.8 | 0.37
| Total |  |  |  | 10.23 | 10.23 | 13.7131 | 22.2382 | 27.2
Transformer Load
| Sr. No | Device | Name | KVA | KW | Total (KW) | HP | P Amp | S Amp
Control | 1 | Transformer-1 (230VAC) | TR-1 | 2 | 1.6 | 1.6 | 2.1448 | 2.7825 | 4.0165
(PLC, HMI, I/O)
| Total |  |  |  | 1.6 | 1.6 | 2.1448 | 2.7825
Total Connected |  |  |  |  | 11.83 | 11.83 | 15.8579 | 29.9825
Total Designed(1.25) |  |  |  |  | 14.7875 | 14.7875 | 19.8224 | 37.4781
2 Nodes

## Dryer Zone Load
|  | Efficiency | 0.8 |  | CYBERNETIK
|  | Power Factor | 0.8 |  | Total KW | 41.44
|  | Line to Line Voltage | 415 |  | Total HP | 55.5496
|  | Single Phase voltage | 230 |  | Total Amp | 72.1499
|  | KW to HP Conversion | 0.746 |  | Design Total KW | 51.8
|  | Design Factor | 1.25 |  | Design Total HP | 69.437
|  | KVA to KW Conversion | 0.8 |  | Design Total Amp | 90.1873
CYBERNETIK MACHINE
Zone | Sr. No | Device | Name | DOL/VFD/Thyrister | KW | Total (KW) | HP | Amp | Drive amp | Motor KW
System | 1 | Dryer Heating Zone Inlet Blower | DHIB01 | VFD | 11 | 11 | 14.7453 | 23.912 | 24 | 11
| 2 | Dryer Heating Zone Dust Collector | DHDC01 | VFD | 11 | 11 | 14.7453 | 23.912 | 24 | 11
| 3 | Dryer Cooling Zone Inlet Blower | DCIB01 | VFD | 5.5 | 5.5 | 7.3727 | 11.956 | 13 | 5.5
| 4 | Dryer Cooling Zone Dust Collector | DCDC01 | VFD | 7.5 | 7.5 | 10.0536 | 16.3037 | 17 | 7.5
| 5 | Dryer Conveyor Motor | DCM01 | VFD | 1.5 | 1.5 | 2.0107 | 3.2607 | 4 | 1.1
| 6 | Dryer Outlet Vibratory feeder-1 | DOVF01 | VFD | 1.5 | 1.5 | 2.0107 | 3.2607 | 4 | 1.1
| 7 | Dryer Outlet Vibratory feeder-2 | DOVF02 | VFD | 1.5 | 1.5 | 2.0107 | 3.2607 | 4 | 1.1
| 8 | Brush Roller Motor-1 | BRM01 | DOL | 0.37 | 0.37 | 0.49598 | 0.80431 | 0.8 | 0.37
| 9 | Brush Roller Motor-2 | BRM02 | DOL | 0.37 | 0.37 | 0.49598 | 0.80431 | 0.8 | 0.37
| Total |  |  |  | 40.24 | 40.24 | 53.941 | 87.4746 | 91.6
Transformer Load
| Sr. No | Device | Name | KVA | KW | Total (KW) | HP | P Amp | S Amp
Control | 1 | Transformer-1 (230VAC) | TR-1 | 1.5 | 1.2 | 1.2 | 1.6086 | 2.0869 | 3.0124
(PLC, HMI, I/O)
| Total |  |  |  | 1.2 | 1.2 | 1.6086 | 2.0869
Total Connected |  |  |  |  | 41.44 | 41.44 | 55.5496 | 93.6869
Total Designed(1.25) |  |  |  |  | 51.8 | 51.8 | 69.437 | 117.1086
2 Nodes

## Packing Zone Load
|  | Efficiency | 0.8 |  | CYBERNETIK
|  | Power Factor | 0.8 |  | Total KW | 16
|  | Line to Line Voltage | 415 |  | Total HP | 21.4477
|  | Single Phase voltage | 230 |  | Total Amp | 27.8571
|  | KW to HP Conversion | 0.746 |  | Design Total KW | 20
|  | Design Factor | 1.25 |  | Design Total HP | 26.8097
|  | KVA to KW Conversion | 0.8 |  | Design Total Amp | 34.8214
CYBERNETIK MACHINE
Zone | Sr. No | Device | Name | DOL/VFD/Thyrister | KW | Total (KW) | HP | Amp | Drive amp | Motor KW
System | 1 | Incliend Belt conveyor | IBC001 | VFD | 1.5 | 1.5 | 2.0107 | 3.2607 | 4 | 1.1
| 2 | Material Storage Vibro-1 | MSV01 | VFD | 1.5 | 1.5 | 2.0107 | 3.2607 | 4 | 1.1
| 3 | Material Storage Vibro-2 | MSV02 | VFD | 1.5 | 1.5 | 2.0107 | 3.2607 | 4 | 1.1
| 4 | Bag Filling Conveyor | BFC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 5 | Bag Sealing & Stiching Conveyor | BSSC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 6 | Bag Stitching Motor | BSTM01 | DOL | 0.75 | 0.75 | 1.0054 | 1.6304 | 1.6 | 0.75
| 7 | Bag Tilting Conveyor | BTC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 8 | Bag Flattening Bottom Conveyor | BFBC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 9 | Bag Flattening Top Conveyor | BFTC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 10 | Metal Detector Conveyor | MDC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 11 | Bag Rejection Conveyor | BRC01 | VFD | 0.75 | 0.75 | 1.0054 | 1.6304 | 2.3 | 0.75
| 12 | Bagging Zone Dust Collector | BDCB01 | DOL | 1.1 | 1.1 | 1.4745 | 2.3912 | 2.4 | 1.1
| Total |  |  |  | 11.6 | 11.6 | 15.5496 | 25.2163 | 32.1
Transformer Load
| Sr. No | Device | Name | KVA | KW | Total (KW) | HP | P Amp | S Amp
Control | 1 | Transformer-1 (230VAC) | TR-1 | 1.5 | 1.2 | 1.2 | 1.6086 | 2.0869 | 3.0124
(PLC, HMI, I/O)
Device | 2 | Transformer-2 (230VAC) | TR-2 | 4 | 3.2 | 3.2 | 4.2895 | 5.565 | 8.0329
Metal Detector (0.5KW)
| 3 | Sealing Station (0.75KW) |  | 0 | 0 | 0 | 0 | 0 | 0
Electro Magnetic Vibro-1 and 2 (0.75X2=1.5KW)
| Total |  |  |  | 4.4 | 4.4 | 5.8981 | 7.6519
Total Connected |  |  |  |  | 16 | 16 | 21.4477 | 39.7519
Total Designed(1.25) |  |  |  |  | 20 | 20 | 26.8097 | 49.6898
2 Nodes

## Chopper IO List
DI | [8 empty] | DO
Sl No | Input Type | Location | Address |  | Input Description | Input Tags | Device | TAG | Sl No | Output Type | Location | Address | Output Description | Output Tags | Device | TAG
[5 empty] | DIGITAL INPUT | Input Tags | [6 empty] | DIGITAL OUTPUT
1 | SDI01 |  | RC:I:1.0 | _ | Chopper-1 E-Stop 1/1 | SDI01_Chopper-1 E-Stop 1/1 | E-Stop Button |  | 1 | SDO01 |  | RC:O:2.0 | Chopper Safety Healhy 1/1 | SDO01_Chopper Safety Healhy 1/1 | Safety Relay (STO)
2 | SDI02 |  | RC:I:1.1 | _ | Chopper-1 E-Stop 1/2 | SDI02_Chopper-1 E-Stop 1/2 | E-Stop Button |  | 2 | SDO02 |  | RC:O:2.1 | Chopper Safety Healhy 1/2 | SDO02_Chopper Safety Healhy 1/2 | Safety Relay (STO)
3 | SDI03 |  | RC:I:1.2 | _ | Chopper-2 E-Stop 1/1 | SDI03_Chopper-2 E-Stop 1/1 | E-Stop Button |  | 3 | SDO03 |  | RC:O:2.2 | Spare | SDO03_Spare
4 | SDI04 |  | RC:I:1.3 | _ | Chopper-2 E-Stop 1/2 | SDI04_Chopper-2 E-Stop 1/2 | E-Stop Button |  | 4 | SDO04 |  | RC:O:2.3 | Spare | SDO04_Spare
5 | SDI05 |  | RC:I:1.4 | _ | Spreader E-Stop 1/1 | SDI05_Spreader E-Stop 1/1 | E-Stop Button |  | 5 | SDO05 |  | RC:O:2.4 | Spare | SDO05_Spare
6 | SDI06 |  | RC:I:1.5 | _ | Spreader E-Stop 1/2 | SDI06_Spreader E-Stop 1/2 | E-Stop Button |  | 6 | SDO06 |  | RC:O:2.5 | Spare | SDO06_Spare
7 | SDI07 |  | RC:I:1.6 | _ | Applicator E-Stop 1/1 | SDI07_Applicator E-Stop 1/1 | E-Stop Button |  | 7 | SDO07 |  | RC:O:2.6 | Air Relief Valve1/1 | SDO07_Air Relief Valve1/1
8 | SDI08 |  | RC:I:1.7 | _ | Applicator E-Stop 1/2 | SDI08_Applicator E-Stop 1/2 | E-Stop Button |  | 8 | SDO08 |  | RC:O:2.7 | Air Relief Valve1/2 | SDO08_Air Relief Valve1/2
1 | DI01 |  | RC:I:3.0 | _ | System Start PB | DI01_System Start PB | Push Button+Lamp |  | 1 | DO01 |  | RC:O:10.0 | Chopper Tower Lamp Red | DO01_Chopper Tower Lamp Red | Tower Lamp
2 | DI02 |  | RC:I:3.1 | _ | System Stop PB | DI02_System Stop PB | Push Button |  | 2 | DO02 |  | RC:O:10.1 | Chopper Tower Lamp Amber | DO02_Chopper Tower Lamp Amber | Tower Lamp
3 | DI03 |  | RC:I:3.2 | _ | System Reset PB | DI03_System Reset PB | Push Button+Lamp |  | 3 | DO03 |  | RC:O:10.2 | Chopper Tower Lamp Green | DO03_Chopper Tower Lamp Green | Tower Lamp
4 | DI04 |  | RC:I:3.3 | _ | Safety Reset PB | DI04_Safety Reset PB | Push Button+Lamp |  | 4 | DO04 |  | RC:O:10.3 | Chopper Tower Lamp Buzzer | DO04_Chopper Tower Lamp Buzzer | Tower Lamp
5 | DI05 |  | RC:I:3.4 | _ | Spare DI | DI05_Spare DI |  |  | 5 | DO05 |  | RC:O:10.4 | Chopper System Start PB Green Lamp | DO05_Chopper System Start PB Green Lamp | Push Button+Lamp
6 | DI06 |  | RC:I:3.5 | _ | Spare DI | DI06_Spare DI |  |  | 6 | DO06 |  | RC:O:10.5 | Chopper System Reset PB Blue Lamp | DO06_Chopper System Reset PB Blue Lamp | Push Button+Lamp
7 | DI07 |  | RC:I:3.6 | _ | 3 Phase Supply Ok | DI07_3 Phase Supply Ok | Phase Failure Relay |  | 7 | DO07 |  | RC:O:10.6 | Chopper System Safety Reset PB Yellow Lamp | DO07_Chopper System Safety Reset PB Yellow Lamp | Push Button+Lamp
8 | DI08 |  | RC:I:3.7 | _ | Chopper Air Pressure Switch | DI08_Chopper Air Pressure Switch | Air Pressure Switch |  | 8 | DO08 |  | RC:O:10.7 | Spare DO | DO08_Spare DO
9 | DI09 |  | RC:I:4.0 | _ | Chopper-1 Local/Remote SS | DI09_Chopper-1 Local/Remote SS | Selector Switch |  | 9 | DO09 |  | RC:O:11.0 | Chopper-1 Start PB Lamp | DO09_Chopper-1 Start PB Lamp
10 | DI10 |  | RC:I:4.1 | _ | Chopper-1 Start PB | DI10_Chopper-1 Start PB | Push Button+Lamp |  | 10 | DO10 |  | RC:O:11.1 | Chopper-1 PU Cylinder-1 Fwd SOV | DO10_Chopper-1 PU Cylinder-1 Fwd SOV
11 | DI11 |  | RC:I:4.2 | _ | Chopper-1 Stop PB | DI11_Chopper-1 Stop PB | Push Button |  | 11 | DO11 |  | RC:O:11.2 | Chopper-1 PU Cylinder-1 Rev SOV | DO11_Chopper-1 PU Cylinder-1 Rev SOV
12 | DI12 |  | RC:I:4.3 | _ | Spare DI | DI12_Spare DI |  |  | 12 | DO12 |  | RC:O:11.3 | Chopper-1 PU Cylinder-2 Fwd SOV | DO12_Chopper-1 PU Cylinder-2 Fwd SOV
13 | DI13 |  | RC:I:4.4 | _ | Chopper-2 Local/Remote SS | DI13_Chopper-2 Local/Remote SS | Selector Switch |  | 13 | DO13 |  | RC:O:11.4 | Chopper-1 PU Cylinder-2 Rev SOV | DO13_Chopper-1 PU Cylinder-2 Rev SOV
14 | DI14 |  | RC:I:4.5 | _ | Chopper-2 Start PB | DI14_Chopper-2 Start PB | Push Button+Lamp |  | 14 | DO14 |  | RC:O:11.5 | Chopper-1 Pressure Roller Cylinder Fwd SOV | DO14_Chopper-1 Pressure Roller Cylinder Fwd SOV
15 | DI15 |  | RC:I:4.6 | _ | Chopper-2 Stop PB | DI15_Chopper-2 Stop PB | Push Button |  | 15 | DO15 |  | RC:O:11.6 | Chopper-1 Pressure Roller Cylinder Rev SOV | DO15_Chopper-1 Pressure Roller Cylinder Rev SOV
16 | DI16 |  | RC:I:4.7 | _ | Spare DI | DI16_Spare DI |  |  | 16 | DO16 |  | RC:O:11.7 | Spare DO | DO16_Spare DO
17 | DI17 |  | RC:I:5.0 | _ | Chopper-1 PU Cylinder-1 Fwd FB | DI17_Chopper-1 PU Cylinder-1 Fwd FB | Reed Switch |  | 17 | DO17 |  | RC:O:12.0 | Chopper-2 Start PB Lamp | DO17_Chopper-2 Start PB Lamp
18 | DI18 |  | RC:I:5.1 | _ | Chopper-1 PU Cylinder-1 Rev FB | DI18_Chopper-1 PU Cylinder-1 Rev FB | Reed Switch |  | 18 | DO18 |  | RC:O:12.1 | Chopper-2 PU Cylinder-1 Fwd SOV | DO18_Chopper-2 PU Cylinder-1 Fwd SOV
19 | DI19 |  | RC:I:5.2 | _ | Chopper-1 PU Cylinder-2 Fwd FB | DI19_Chopper-1 PU Cylinder-2 Fwd FB | Reed Switch |  | 19 | DO19 |  | RC:O:12.2 | Chopper-2 PU Cylinder-1 Rev SOV | DO19_Chopper-2 PU Cylinder-1 Rev SOV
20 | DI20 |  | RC:I:5.3 | _ | Chopper-1 PU Cylinder-2 Rev FB | DI20_Chopper-1 PU Cylinder-2 Rev FB | Reed Switch |  | 20 | DO20 |  | RC:O:12.3 | Chopper-2 PU Cylinder-2 Fwd SOV | DO20_Chopper-2 PU Cylinder-2 Fwd SOV
21 | DI21 |  | RC:I:5.4 | _ | Chopper-1 Pressure Roller Cylinder Fwd FB | DI21_Chopper-1 Pressure Roller Cylinder Fwd FB | Reed Switch |  | 21 | DO21 |  | RC:O:12.4 | Chopper-2 PU Cylinder-2 Rev SOV | DO21_Chopper-2 PU Cylinder-2 Rev SOV
22 | DI22 |  | RC:I:5.5 | _ | Chopper-1 Pressure Roller Cylinder Rev FB | DI22_Chopper-1 Pressure Roller Cylinder Rev FB | Reed Switch |  | 22 | DO22 |  | RC:O:12.5 | Chopper-2 Pressure Roller Cylinder Fwd SOV | DO22_Chopper-2 Pressure Roller Cylinder Fwd SOV
23 | DI23 |  | RC:I:5.6 | _ | Spare DI | DI23_Spare DI |  |  | 23 | DO23 |  | RC:O:12.6 | Chopper-2 Pressure Roller Cylinder Rev SOV | DO23_Chopper-2 Pressure Roller Cylinder Rev SOV
24 | DI24 |  | RC:I:5.7 | _ | Spare DI | DI24_Spare DI |  |  | 24 | DO24 |  | RC:O:12.7 | Spare DO | DO24_Spare DO
25 | DI25 |  | RC:I:6.0 | _ | Chopper-2 PU Cylinder-1 Fwd FB | DI25_Chopper-2 PU Cylinder-1 Fwd FB | Reed Switch |  | 25 | DO25 |  | RC:O:13.0 | Spreader Start PB Lamp | DO25_Spreader Start PB Lamp
26 | DI26 |  | RC:I:6.1 | _ | Chopper-2 PU Cylinder-1 Rev FB | DI26_Chopper-2 PU Cylinder-1 Rev FB | Reed Switch |  | 26 | DO26 |  | RC:O:13.1 | Applicator Start PB Lamp | DO26_Applicator Start PB Lamp
27 | DI27 |  | RC:I:6.2 | _ | Chopper-2 PU Cylinder-2 Fwd FB | DI27_Chopper-2 PU Cylinder-2 Fwd FB | Reed Switch |  | 27 | DO27 |  | RC:O:13.2 | Spare DO | DO27_Spare DO
28 | DI28 |  | RC:I:6.3 | _ | Chopper-2 PU Cylinder-2 Rev FB | DI28_Chopper-2 PU Cylinder-2 Rev FB | Reed Switch |  | 28 | DO28 |  | RC:O:13.3 | Spare DO | DO28_Spare DO
29 | DI29 |  | RC:I:6.4 | _ | Chopper-2 Pressure Roller Cylinder Fwd FB | DI29_Chopper-2 Pressure Roller Cylinder Fwd FB | Reed Switch |  | 29 | DO29 |  | RC:O:13.4 | Spare DO | DO29_Spare DO
30 | DI30 |  | RC:I:6.5 | _ | Chopper-2 Pressure Roller Cylinder Rev FB | DI30_Chopper-2 Pressure Roller Cylinder Rev FB | Reed Switch |  | 30 | DO30 |  | RC:O:13.5 | Spare DO | DO30_Spare DO
31 | DI31 |  | RC:I:6.6 | _ | Spare DI | DI31_Spare DI |  |  | 31 | DO31 |  | RC:O:13.6 | Spare DO | DO31_Spare DO
32 | DI32 |  | RC:I:6.7 | _ | Spare DI | DI32_Spare DI |  |  | 32 | DO32 |  | RC:O:13.7 | Spare DO | DO32_Spare DO
33 | DI33 |  | RC:I:7.0 | _ | Spreader Local/Remote SS | DI33_Spreader Local/Remote SS | Selector Switch
34 | DI34 |  | RC:I:7.1 | _ | Spreader Start PB | DI34_Spreader Start PB | Push Button+Lamp
35 | DI35 |  | RC:I:7.2 | _ | Spreader Stop PB | DI35_Spreader Stop PB | Push Button
36 | DI36 |  | RC:I:7.3 | _ | Spare DI | DI36_Spare DI
37 | DI37 |  | RC:I:7.4 | _ | Spare DI | DI37_Spare DI
38 | DI38 |  | RC:I:7.5 | _ | Applicator Local/Remote SS | DI38_Applicator Local/Remote SS | Selector Switch
39 | DI39 |  | RC:I:7.6 | _ | Applicator Start PB | DI39_Applicator Start PB | Push Button+Lamp
40 | DI40 |  | RC:I:7.7 | _ | Applicator Stop PB | DI40_Applicator Stop PB | Push Button
41 | DI41 |  | RC:I:8.0 | _ | Spare DI | DI41_Spare DI
42 | DI42 |  | RC:I:8.1 | _ | Chopper Motor-1 MPCB Healthy | DI42_Chopper Motor-1 MPCB Healthy | MPCB Contact
43 | DI43 |  | RC:I:8.2 | _ | Chopper Motor-2 MPCB Healthy | DI43_Chopper Motor-2 MPCB Healthy | MPCB Contact
44 | DI44 |  | RC:I:8.3 | _ | Anti-Static Coating Roller MPCB Healthy | DI44_Anti-Static Coating Roller MPCB Healthy | MPCB Contact
45 | DI45 |  | RC:I:8.4 | _ | Spreader Motor-2 MPCB Healthy | DI45_Spreader Motor-2 MPCB Healthy | MPCB Contact
46 | DI46 |  | RC:I:8.5 | _ | Feeders-1 MPCB Healthy | DI46_Feeders-1 MPCB Healthy | MPCB Contact
47 | DI47 |  | RC:I:8.6 | _ | Feeders-2 MPCB Healthy | DI47_Feeders-2 MPCB Healthy | MPCB Contact
48 | DI48 |  | RC:I:8.7 | _ | Feeders-3 MPCB Healthy | DI48_Feeders-3 MPCB Healthy | MPCB Contact
49 | DI49 |  | RC:I:9.0 | _ | Spare DI | DI49_Spare DI
50 | DI50 |  | RC:I:9.1 | _ | Chopper Motor-1 Disconnector FB | DI50_Chopper Motor-1 Disconnector FB | LDS switch
51 | DI51 |  | RC:I:9.2 | _ | Chopper Motor-2 Disconnector FB | DI51_Chopper Motor-2 Disconnector FB | LDS switch
52 | DI52 |  | RC:I:9.3 | _ | Anti-Static Coating Roller Disconnector FB | DI52_Anti-Static Coating Roller Disconnector FB | LDS switch
53 | DI53 |  | RC:I:9.4 | _ | Spreader Motor-2 Disconnector FB | DI53_Spreader Motor-2 Disconnector FB | LDS switch
54 | DI54 |  | RC:I:9.5 | _ | Spare DI | DI54_Spare DI
55 | DI55 |  | RC:I:9.6 | _ | Spare DI | DI55_Spare DI
56 | DI56 |  | RC:I:9.7 | _ | Spare DI | DI56_Spare DI

## Dryer IO List
DI | [8 empty] | DO
Sl No | Input Type | Location | Address |  | Input Description | Input Tags | Device | TAG | Sl No | Output Type | Location | Address | Output Description | Output Tags | Device | TAG
[5 empty] | DIGITAL INPUT | Input Tags | [6 empty] | DIGITAL OUTPUT
1 | SDI01 |  | RD:1:I.0 | _ | Dryer Infeed E-Stop 1/1 | SDI01_Dryer Infeed E-Stop 1/1 | E-Stop Button |  | 1 | SDO01 |  | RD:O:2.0 | Dryer Safety Healhy 1/1 | SDO01_Dryer Safety Healhy 1/1 | Safety Relay (STO)
2 | SDI02 |  | RD:1:I.1 | _ | Dryer Infeed E-Stop 1/2 | SDI02_Dryer Infeed E-Stop 1/2 | E-Stop Button |  | 2 | SDO02 |  | RD:O:2.1 | Dryer Safety Healhy 1/2 | SDO02_Dryer Safety Healhy 1/2 | Safety Relay (STO)
3 | SDI03 |  | RD:1:I.2 | _ | Dryer Outfeed E-Stop 1/1 | SDI03_Dryer Outfeed E-Stop 1/1 | E-Stop Button |  | 3 | SDO03 |  | RD:O:2.2 | Spare | SDO03_Spare
4 | SDI04 |  | RD:1:I.3 | _ | Dryer Outfeed E-Stop 1/2 | SDI04_Dryer Outfeed E-Stop 1/2 | E-Stop Button |  | 4 | SDO04 |  | RD:O:2.3 | Spare | SDO04_Spare
5 | SDI05 |  | RD:1:I.4 | _ | Spare | SDI05_Spare |  |  | 5 | SDO05 |  | RD:O:2.4 | Spare | SDO05_Spare
6 | SDI06 |  | RD:1:I.5 | _ | Spare | SDI06_Spare |  |  | 6 | SDO06 |  | RD:O:2.5 | Spare | SDO06_Spare
7 | SDI07 |  | RD:1:I.6 | _ | Spare | SDI07_Spare |  |  | 7 | SDO07 |  | RD:O:2.6 | Air Relief Valve1/1 | SDO07_Air Relief Valve1/1
8 | SDI08 |  | RD:1:I.7 | _ | Spare | SDI08_Spare |  |  | 8 | SDO08 |  | RD:O:2.7 | Air Relief Valve1/2 | SDO08_Air Relief Valve1/2
1 | DI01 |  | RD:3:I.0 | _ | System Start PB | DI01_System Start PB | Push Button+Lamp |  | 1 | DO01 |  | RD:7:O.0 | Dryer Tower Lamp Red | DO01_Dryer Tower Lamp Red | Tower Lamp
2 | DI02 |  | RD:3:I.1 | _ | System Stop PB | DI02_System Stop PB | Push Button |  | 2 | DO02 |  | RD:7:O.1 | Dryer Tower Lamp Amber | DO02_Dryer Tower Lamp Amber | Tower Lamp
3 | DI03 |  | RD:3:I.2 | _ | System Reset PB | DI03_System Reset PB | Push Button+Lamp |  | 3 | DO03 |  | RD:7:O.2 | Dryer Tower Lamp Green | DO03_Dryer Tower Lamp Green | Tower Lamp
4 | DI04 |  | RD:3:I.3 | _ | Safety Reset PB | DI04_Safety Reset PB | Push Button+Lamp |  | 4 | DO04 |  | RD:7:O.3 | Dryer Tower Lamp Buzzer | DO04_Dryer Tower Lamp Buzzer | Tower Lamp
5 | DI05 |  | RD:3:I.4 | _ | Spare DI | DI05_Spare DI |  |  | 5 | DO05 |  | RD:7:O.4 | Dryer System Start PB Green Lamp | DO05_Dryer System Start PB Green Lamp | Push Button+Lamp
6 | DI06 |  | RD:3:I.5 | _ | Spare DI | DI06_Spare DI |  |  | 6 | DO06 |  | RD:7:O.5 | Dryer System Reset PB Blue Lamp | DO06_Dryer System Reset PB Blue Lamp | Push Button+Lamp
7 | DI07 |  | RD:3:I.6 | _ | 3 Phase Supply Ok | DI07_3 Phase Supply Ok | Phase Failure Relay |  | 7 | DO07 |  | RD:7:O.6 | Dryer System Safety Reset PB Yellow Lamp | DO07_Dryer System Safety Reset PB Yellow Lamp | Push Button+Lamp
8 | DI08 |  | RD:3:I.7 | _ | Dryer Air Pressure | DI08_Dryer Air Pressure | Air Pressure Switch |  | 8 | DO08 |  | RD:7:O.7 | Spare DO | DO08_Spare DO
9 | DI09 |  | RD:4:I.0 | _ | Spare DI | DI09_Spare DI |  |  | 9 | DO09 |  | RD:8:O.0 | Dryer Outlet Vibratory feeder-1 Enable | DO09_Dryer Outlet Vibratory feeder-1 Enable | Contactor
10 | DI10 |  | RD:4:I.1 | _ | Spare DI | DI10_Spare DI |  |  | 10 | DO10 |  | RD:8:O.1 | Dryer Outlet Vibratory feeder-2 Enable | DO10_Dryer Outlet Vibratory feeder-2 Enable | Contactor
11 | DI11 |  | RD:4:I.2 | _ | Spare DI | DI11_Spare DI |  |  | 11 | DO11 |  | RD:8:O.2 | Dryer Heating Zone Dust Collector PV01 | DO11_Dryer Heating Zone Dust Collector PV01 | Pulse Valve Coil
12 | DI12 |  | RD:4:I.3 | _ | Spare DI | DI12_Spare DI |  |  | 12 | DO12 |  | RD:8:O.3 | Dryer Heating Zone Dust Collector PV02 | DO12_Dryer Heating Zone Dust Collector PV02 | Pulse Valve Coil
13 | DI13 |  | RD:4:I.4 | _ | Dryer Heating Zone Inlet Blower Disconnector FB | DI13_Dryer Heating Zone Inlet Blower Disconnector FB | Disconnector Switch FB |  | 13 | DO13 |  | RD:8:O.4 | Dryer Heating Zone Dust Collector PV03 | DO13_Dryer Heating Zone Dust Collector PV03 | Pulse Valve Coil
14 | DI14 |  | RD:4:I.5 | _ | Dryer Heating Zone Dust Collector Disconnector FB | DI14_Dryer Heating Zone Dust Collector Disconnector FB | Disconnector Switch FB |  | 14 | DO14 |  | RD:8:O.5 | Dryer Cooling Zone Dust Collector PV01 | DO14_Dryer Cooling Zone Dust Collector PV01 | Pulse Valve Coil
15 | DI15 |  | RD:4:I.6 | _ | Dryer Cooling Zone Inlet Blower Disconnector FB | DI15_Dryer Cooling Zone Inlet Blower Disconnector FB | Disconnector Switch FB |  | 15 | DO15 |  | RD:8:O.6 | Dryer Cooling Zone Dust Collector PV02 | DO15_Dryer Cooling Zone Dust Collector PV02 | Pulse Valve Coil
16 | DI16 |  | RD:4:I.7 | _ | Dryer Cooling Zone Dust Collector Disconnector FB | DI16_Dryer Cooling Zone Dust Collector Disconnector FB | Disconnector Switch FB |  | 16 | DO16 |  | RD:8:O.7 | Dryer Cooling Zone Dust Collector PV03 | DO16_Dryer Cooling Zone Dust Collector PV03 | Pulse Valve Coil
17 | DI17 |  | RD:5:I.0 | _ | Dryer Conveyor Motor Disconnector FB | DI17_Dryer Conveyor Motor Disconnector FB | Disconnector Switch FB |  | 17 | DO17 |  | RD:9:O.0 | Spare DO | DO17_Spare DO
18 | DI18 |  | RD:5:I.1 | _ | Dryer Outlet Vibratory feeder-1 MPCB Healthy | DI18_Dryer Outlet Vibratory feeder-1 MPCB Healthy | MPCB Contact |  | 18 | DO18 |  | RD:9:O.1 | Spare DO | DO18_Spare DO
19 | DI19 |  | RD:5:I.2 | _ | Dryer Outlet Vibratory feeder-2 MPCB Healthy | DI19_Dryer Outlet Vibratory feeder-2 MPCB Healthy | MPCB Contact |  | 19 | DO19 |  | RD:9:O.2 | Spare DO | DO19_Spare DO
20 | DI20 |  | RD:5:I.3 | _ | Gas Burner MPCB Healthy | DI20_Gas Burner MPCB Healthy | MPCB Contact |  | 20 | DO20 |  | RD:9:O.3 | Spare DO | DO20_Spare DO
21 | DI21 |  | RD:5:I.4 | _ | Dryer Outlet Vibratory feeder-1 Disconnector FB | DI21_Dryer Outlet Vibratory feeder-1 Disconnector FB | Disconnector Switch FB |  | 21 | DO21 |  | RD:9:O.4 | Gas Burner Enable | DO21_Gas Burner Enable | Contact
22 | DI22 |  | RD:5:I.5 | _ | Dryer Outlet Vibratory feeder-2 Disconnector FB | DI22_Dryer Outlet Vibratory feeder-2 Disconnector FB | Disconnector Switch FB |  | 22 | DO22 |  | RD:9:O.5 | Spare DO | DO22_Spare DO
23 | DI23 |  | RD:5:I.6 | _ | Gas Burner Disconnector FB | DI23_Gas Burner Disconnector FB | Disconnector Switch FB |  | 23 | DO23 |  | RD:9:O.6 | Spare DO | DO23_Spare DO
24 | DI24 |  | RD:5:I.7 | _ | Spare DI | DI24_Spare DI |  |  | 24 | DO24 |  | RD:9:O.7 | Spare DO | DO24_Spare DO
25 | DI25 |  | RD:6:I.0 | _ | Gas Burner Healthy FB | DI25_Gas Burner Healthy FB | Contact |  | 25 | DO25 |  | RD:10:O.0 | Spare DO | DO25_Spare DO
26 | DI26 |  | RD:6:I.1 | _ | Spare DI | DI26_Spare DI |  |  | 26 | DO26 |  | RD:10:O.1 | Spare DO | DO26_Spare DO
27 | DI27 |  | RD:6:I.2 | _ | Dryer Heating Zone Dust Collector Level High | DI27_Dryer Heating Zone Dust Collector Level High | Level Sensor |  | 27 | DO27 |  | RD:10:O.2 | Spare DO | DO27_Spare DO
28 | DI28 |  | RD:6:I.3 | _ | Dryer Cooling Zone Dust Collector Level High | DI28_Dryer Cooling Zone Dust Collector Level High | Level Sensor |  | 28 | DO28 |  | RD:10:O.3 | Spare DO | DO28_Spare DO
29 | DI29 |  | RD:6:I.4 | _ | Spare DI | DI29_Spare DI |  |  | 29 | DO29 |  | RD:10:O.4 | Spare DO | DO29_Spare DO
30 | DI30 |  | RD:6:I.5 | _ | Spare DI | DI30_Spare DI |  |  | 30 | DO30 |  | RD:10:O.5 | Spare DO | DO30_Spare DO
31 | DI31 |  | RD:6:I.6 | _ | Spare DI | DI31_Spare DI |  |  | 31 | DO31 |  | RD:10:O.6 | Spare DO | DO31_Spare DO
32 | DI32 |  | RD:6:I.7 | _ | Spare DI | DI32_Spare DI |  |  | 32 | DO32 |  | RD:10:O.7 | Spare DO | DO32_Spare DO
Sl No | Input Type | Location | Address |  | Input Description | Input Tags | Device | TAG | Sl No | Output Type | Location | Address | Output Description | Output Tags | Device | TAG
[5 empty] | ANALOG INPUT | Input Tags | [6 empty] | ANALOG OUTPUT
1 | AI01 |  | RD:11:I.Ch0 | _ | Gas Burner Inlet Temperature | AI01_Gas Burner Inlet Temperature | Temperature Transmitter |  | 1 | AO01 |  | RD:13:O.Ch0 | Gas Burner Flame Control Signal | AO01_Gas Burner Flame Control Signal | Burner Controller
2 | AI02 |  | RD:11:I.Ch1 | _ | Gas Burner Outlet Temperature | AI02_Gas Burner Outlet Temperature | Temperature Transmitter |  | 2 | AO02 |  | RD:13:O.Ch1 | Spare AO | AO02_Spare AO
3 | AI03 |  | RD:11:I.Ch2 | _ | Dryer Heating Zone-1 Temperature | AI03_Dryer Heating Zone-1 Temperature | Temperature Transmitter
4 | AI04 |  | RD:11:I.Ch3 | _ | Dryer Heating Zone-2 Temperature | AI04_Dryer Heating Zone-2 Temperature | Temperature Transmitter
5 | AI05 |  | RD:12:I.Ch0 | _ | Dryer Heating Zone-3 Temperature | AI05_Dryer Heating Zone-3 Temperature | Temperature Transmitter
6 | AI06 |  | RD:12:I.Ch1 | _ | Cooling Air Inlet Temperature | AI06_Cooling Air Inlet Temperature | Temperature Transmitter
7 | AI07 |  | RD:12:I.Ch2 | _ | Cooling Air Outlet Temperature | AI07_Cooling Air Outlet Temperature | Temperature Transmitter
8 | AI08 |  | RD:12:I.Ch3 | _ | Dryer Cooling Zone Temperature | AI08_Dryer Cooling Zone Temperature | Temperature Transmitter
9 | AI09 |  | RD:13:I.Ch0 | _ | Dryer Heating Zone Dust Collector Pressure Transmitter | AI09_Dryer Heating Zone Dust Collector Pressure Transmitter | Pressure Transmitter
10 | AI10 |  | RD:13:I.Ch1 | _ | Dryer Cooling Zone Dust Collector Pressure Transmitter | AI10_Dryer Cooling Zone Dust Collector Pressure Transmitter | Pressure Transmitter
11 | AI11 |  | RD:13:I.Ch2 | _ | Spare AI | AI11_Spare AI
12 | AI12 |  | RD:13:I.Ch3 | _ | Spare AI | AI12_Spare AI

## Packing IO List
DI | [8 empty] | DO
Sl No | Input Type | Location | Address |  | Input Description | Input Tags | Device | TAG | Sl No | Output Type | Location | Address | Output Description | Output Tags | Device | TAG
[5 empty] | DIGITAL INPUT | Input Tags | [6 empty] | DIGITAL OUTPUT
1 | SDI01 |  | RP:1:I.0 | _ | Bag Filling Area E-Stop 1/1 | SDI01_Bag Filling Area E-Stop 1/1 | E-Stop Button | [PLC]RIO01_DI[01] |  | SDO01 |  | RP:2:O.0 | Packing Machine Safety Healhy 1/1 | SDO01_Packing Machine Safety Healhy 1/1 | Safety Relay (STO)
2 | SDI02 |  | RP:1:I.1 | _ | Bag Filling Area E-Stop 1/2 | SDI02_Bag Filling Area E-Stop 1/2 | E-Stop Button | [PLC]RIO01_DI[02] |  | SDO02 |  | RP:2:O.1 | Packing Machine Safety Healhy 1/2 | SDO02_Packing Machine Safety Healhy 1/2 | Safety Relay (STO)
3 | SDI03 |  | RP:1:I.2 | _ | Bag Rejection Area E-Stop 1/1 | SDI03_Bag Rejection Area E-Stop 1/1 | E-Stop Button | [PLC]RIO01_DI[03] |  | SDO03 |  | RP:2:O.2 | Air Service Unit Coil-1 Enable | SDO03_Air Service Unit Coil-1 Enable | Air Service Unit Coil
4 | SDI04 |  | RP:1:I.3 | _ | Bag Rejection Area E-Stop 1/2 | SDI04_Bag Rejection Area E-Stop 1/2 | E-Stop Button | [PLC]RIO01_DI[04] |  | SDO04 |  | RP:2:O.3 | Air Service Unit Coil-2 Enable | SDO04_Air Service Unit Coil-2 Enable | Air Service Unit Coil
5 | SDI05 |  | RP:1:I.4 | _ | Spare DI | SDI05_Spare DI |  | [PLC]RIO01_DI[05] |  | SDO05 |  | RP:2:O.4 |  | SDO05_
6 | SDI06 |  | RP:1:I.5 | _ | Spare DI | SDI06_Spare DI |  | [PLC]RIO01_DI[06] |  | SDO06 |  | RP:2:O.5 |  | SDO06_
7 | SDI07 |  | RP:1:I.6 | _ | Spare DI | SDI07_Spare DI |  | [PLC]RIO01_DI[07] |  | SDO07 |  | RP:2:O.6 |  | SDO07_
8 | SDI08 |  | RP:1:I.7 | _ | Spare DI | SDI08_Spare DI |  | [PLC]RIO01_DI[08] |  | SDO08 |  | RP:2:O.7 |  | SDO08_
1 | DI01 |  | RP:3:I.0 | _ | Packing Start PB | DI01_Packing Start PB | Push Button+Lamp | [PLC]RIO01_DI[09] |  | DO01 |  | RP:14:O.0 | Packing Tower Lamp Red | DO01_Packing Tower Lamp Red | Tower Lamp
2 | DI02 |  | RP:3:I.1 | _ | Packing Stop PB | DI02_Packing Stop PB | Push Button | [PLC]RIO01_DI[10] |  | DO02 |  | RP:14:O.1 | Packing Tower Lamp Amber | DO02_Packing Tower Lamp Amber | Tower Lamp
3 | DI03 |  | RP:3:I.2 | _ | Packing System Reset PB | DI03_Packing System Reset PB | Push Button+Lamp | [PLC]RIO01_DI[11] |  | DO03 |  | RP:14:O.2 | Packing Tower Lamp Green | DO03_Packing Tower Lamp Green | Tower Lamp
4 | DI04 |  | RP:3:I.3 | _ | Packing System Safety Reset PB | DI04_Packing System Safety Reset PB | Push Button+Lamp | [PLC]RIO01_DI[12] |  | DO04 |  | RP:14:O.3 | Packing Tower Lamp Buzzer | DO04_Packing Tower Lamp Buzzer | Tower Lamp
5 | DI05 |  | RP:3:I.4 | _ | Spare DI | DI05_Spare DI |  | [PLC]RIO01_DI[13] |  | DO05 |  | RP:14:O.4 | Packing System Start PB Green Lamp | DO05_Packing System Start PB Green Lamp | Push Button+Lamp
6 | DI06 |  | RP:3:I.5 | _ | 3 Phase Supply Ok | DI06_3 Phase Supply Ok | Air Pressure Switch | [PLC]RIO01_DI[14] |  | DO06 |  | RP:14:O.5 | Packing System Reset PB Blue Lamp | DO06_Packing System Reset PB Blue Lamp | Push Button+Lamp
7 | DI07 |  | RP:3:I.6 | _ | Packing Air Pressure Switch | DI07_Packing Air Pressure Switch | Phase Failure Relay | [PLC]RIO01_DI[15] |  | DO07 |  | RP:14:O.6 | Packing System Safety Reset PB Yellow Lamp | DO07_Packing System Safety Reset PB Yellow Lamp | Push Button+Lamp
8 | DI08 |  | RP:3:I.7 | _ | Spare DI | DI08_Spare DI |  | [PLC]RIO01_DI[16] |  | DO08 |  | RP:14:O.7 | Spare DO | DO08_Spare DO
9 | DI09 |  | RP:4:I.0 | _ | Incliend Belt conveyor Disconnector FB | DI09_Incliend Belt conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[17] |  | DO09 |  | RP:15:O.0 | Electro Magnetic Coarse Vibro Enable | DO09_Electro Magnetic Coarse Vibro Enable | Contact
10 | DI10 |  | RP:4:I.1 | _ | Material Storage Vibro-1 Disconnector FB | DI10_Material Storage Vibro-1 Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[18] |  | DO10 |  | RP:15:O.1 | Electro Magnetic Fine Vibro Enable | DO10_Electro Magnetic Fine Vibro Enable | Contact
11 | DI11 |  | RP:4:I.2 | _ | Material Storage Vibro-2 Disconnector FB | DI11_Material Storage Vibro-2 Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[19] |  | DO11 |  | RP:15:O.2 | Bag Stitching Motor Enable | DO11_Bag Stitching Motor Enable | Contactor
12 | DI12 |  | RP:4:I.3 | _ | Bag Filling Conveyor Disconnector FB | DI12_Bag Filling Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[20] |  | DO12 |  | RP:15:O.3 | Bagging Zone Dust Collector Enable | DO12_Bagging Zone Dust Collector Enable | Contactor
13 | DI13 |  | RP:4:I.4 | _ | Bag Sealing & Stiching Conveyor Disconnector FB | DI13_Bag Sealing & Stiching Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[21] |  | DO13 |  | RP:15:O.4 | Bag Sealing Machine Enable | DO13_Bag Sealing Machine Enable | Contact
14 | DI14 |  | RP:4:I.5 | _ | Bag Stitching Motor Trip Healthy | DI14_Bag Stitching Motor Trip Healthy | MPCB Contact | [PLC]RIO01_DI[22] |  | DO14 |  | RP:15:O.5 | Spare DO | DO14_Spare DO
15 | DI15 |  | RP:4:I.6 | _ | Bag Tilting Conveyor Disconnector FB | DI15_Bag Tilting Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[23] |  | DO15 |  | RP:15:O.6 | Spare DO | DO15_Spare DO
16 | DI16 |  | RP:4:I.7 | _ | Bag Flattening Bottom Conveyor Disconnector FB | DI16_Bag Flattening Bottom Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[24] |  | DO16 |  | RP:15:O.7 | Spare DO | DO16_Spare DO
17 | DI17 |  | RP:5:I.0 | _ | Bag Flattening Top Conveyor Disconnector FB | DI17_Bag Flattening Top Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[25] |  | DO17 |  | RP:16:O.0 | Diverter Flap Cylinder FWD SOV | DO17_Diverter Flap Cylinder FWD SOV | SOV Coil
18 | DI18 |  | RP:5:I.1 | _ | Metal Detector Conveyor Disconnector FB | DI18_Metal Detector Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[26] |  | DO18 |  | RP:16:O.1 | Diverter Flap Cylinder REV SOV | DO18_Diverter Flap Cylinder REV SOV | SOV Coil
19 | DI19 |  | RP:5:I.2 | _ | Bag Rejection Conveyor Disconnector FB | DI19_Bag Rejection Conveyor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[27] |  | DO19 |  | RP:16:O.2 | Filling Station Bag Clamp-1/2 Open SOV | DO19_Filling Station Bag Clamp-1/2 Open SOV | SOV Coil
20 | DI20 |  | RP:5:I.3 | _ | Bagging Zone Dust Collector Trip Healthy | DI20_Bagging Zone Dust Collector Trip Healthy | MPCB Contact | [PLC]RIO01_DI[28] |  | DO20 |  | RP:16:O.3 | Filling Station Bag Clamp-1/2 Open SOV | DO20_Filling Station Bag Clamp-1/2 Open SOV | SOV Coil
21 | DI21 |  | RP:5:I.4 | _ | Electro Magnetic Coarse Vibro Trip Healthy | DI21_Electro Magnetic Coarse Vibro Trip Healthy | MCB Contact | [PLC]RIO01_DI[29] |  | DO21 |  | RP:16:O.4 | Filling Station Bag Side Flap-1/2 Open SOV | DO21_Filling Station Bag Side Flap-1/2 Open SOV | SOV Coil
22 | DI22 |  | RP:5:I.5 | _ | Electro Magnetic Fine Vibro Trip Healthy | DI22_Electro Magnetic Fine Vibro Trip Healthy | MCB Contact | [PLC]RIO01_DI[30] |  | DO22 |  | RP:16:O.5 | Filling Station Bag Side Flap-1/2 Close SOV | DO22_Filling Station Bag Side Flap-1/2 Close SOV | SOV Coil
23 | DI23 |  | RP:5:I.6 | _ | Band Sealer Machine Trip Healthy | DI23_Band Sealer Machine Trip Healthy | MCB Contact | [PLC]RIO01_DI[31] |  | DO23 |  | RP:16:O.6 | Filling Station Conveyor Up SOV | DO23_Filling Station Conveyor Up SOV | SOV Coil
24 | DI24 |  | RP:5:I.7 | _ | Spare DI | DI24_Spare DI |  | [PLC]RIO01_DI[32] |  | DO24 |  | RP:16:O.7 | Filling Station Conveyor Dn SOV | DO24_Filling Station Conveyor Dn SOV | SOV Coil
25 | DI25 |  | RP:6:I.0 | _ | Spare DI | DI25_Spare DI |  | [PLC]RIO01_DI[33] |  | DO25 |  | RP:17:O.0 | Stitching Station Thread Cutter Cylinder Fwd SOV | DO25_Stitching Station Thread Cutter Cylinder Fwd SOV | SOV Coil
26 | DI26 |  | RP:6:I.1 | _ | Bag Stitching Motor Disconnector FB | DI26_Bag Stitching Motor Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[34] |  | DO26 |  | RP:17:O.1 | Stitching Station Thread Cutter Cylinder Rev SOV | DO26_Stitching Station Thread Cutter Cylinder Rev SOV | SOV Coil
27 | DI27 |  | RP:6:I.2 | _ | Bagging Zone Dust Collector Disconnector FB | DI27_Bagging Zone Dust Collector Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[35] |  | DO27 |  | RP:17:O.2 | Rejection Station Pusher Cyl Forward SOV | DO27_Rejection Station Pusher Cyl Forward SOV | SOV Coil
28 | DI28 |  | RP:6:I.3 | _ | Electro Magnetic Coarse Vibro Disconnector FB | DI28_Electro Magnetic Coarse Vibro Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[36] |  | DO28 |  | RP:17:O.3 | Rejection Station Pusher Cyl Reverse SOV | DO28_Rejection Station Pusher Cyl Reverse SOV | SOV Coil
29 | DI29 |  | RP:6:I.4 | _ | Electro Magnetic Fine Vibro Disconnector FB | DI29_Electro Magnetic Fine Vibro Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[37] |  | DO29 |  | RP:17:O.4 | Spare DO | DO29_Spare DO
30 | DI30 |  | RP:6:I.5 | _ | Band Sealer Machine Disconnector FB | DI30_Band Sealer Machine Disconnector FB | Disconnector Switch FB | [PLC]RIO01_DI[38] |  | DO30 |  | RP:17:O.5 | Packing Zone Dust Collector PV01 | DO30_Packing Zone Dust Collector PV01 | Pulse Valve Coil
31 | DI31 |  | RP:6:I.6 | _ | Spare DI | DI31_Spare DI |  | [PLC]RIO01_DI[39] |  | DO31 |  | RP:17:O.6 | Packing Zone Dust Collector PV02 | DO31_Packing Zone Dust Collector PV02 | Pulse Valve Coil
32 | DI32 |  | RP:6:I.7 | _ | Spare DI | DI32_Spare DI |  | [PLC]RIO01_DI[40] |  | DO32 |  | RP:17:O.7 | Spare DO | DO32_Spare DO
33 | DI33 |  | RP:7:I.0 | _ | Diverter Flap Cylinder FWD FB | DI33_Diverter Flap Cylinder FWD FB | Reed Switch | [PLC]RIO01_DI[41] |  | DO33 |  | RP:18:O.0 | Spare DO | DO33_Spare DO
34 | DI34 |  | RP:7:I.1 | _ | Diverter Flap Cylinder REV FB | DI34_Diverter Flap Cylinder REV FB | Reed Switch | [PLC]RIO01_DI[42] |  | DO34 |  | RP:18:O.1 | Spare DO | DO34_Spare DO
35 | DI35 |  | RP:7:I.2 | _ | Filling Station Bag Clamp-1 Open FB | DI35_Filling Station Bag Clamp-1 Open FB | Reed Switch | [PLC]RIO01_DI[43] |  | DO35 |  | RP:18:O.2 | Spare DO | DO35_Spare DO
36 | DI36 |  | RP:7:I.3 | _ | Filling Station Bag Clamp-1 CloseFB | DI36_Filling Station Bag Clamp-1 CloseFB | Reed Switch | [PLC]RIO01_DI[44] |  | DO36 |  | RP:18:O.3 | Spare DO | DO36_Spare DO
37 | DI37 |  | RP:7:I.4 | _ | Filling Station Bag Clamp-2 Open FB | DI37_Filling Station Bag Clamp-2 Open FB | Reed Switch | [PLC]RIO01_DI[45] |  | DO37 |  | RP:18:O.4 | Spare DO | DO37_Spare DO
38 | DI38 |  | RP:7:I.5 | _ | Filling Station Bag Clamp-2 Close FB | DI38_Filling Station Bag Clamp-2 Close FB | Reed Switch | [PLC]RIO01_DI[46] |  | DO38 |  | RP:18:O.5 | Spare DO | DO38_Spare DO
39 | DI39 |  | RP:7:I.6 | _ | Filling Station Bag Side Flap-1 Open FB | DI39_Filling Station Bag Side Flap-1 Open FB | Reed Switch | [PLC]RIO01_DI[47] |  | DO39 |  | RP:18:O.6 | Spare DO | DO39_Spare DO
40 | DI40 |  | RP:7:I.7 | _ | Filling Station Bag Side Flap-1 Close FB | DI40_Filling Station Bag Side Flap-1 Close FB | Reed Switch | [PLC]RIO01_DI[48] |  | DO40 |  | RP:18:O.7 | Spare DO | DO40_Spare DO
41 | DI41 |  | RP:8:I.0 | _ | Filling Station Bag Side Flap-2 Open FB | DI41_Filling Station Bag Side Flap-2 Open FB | Reed Switch | [PLC]RIO01_DI[49]
42 | DI42 |  | RP:8:I.1 | _ | Filling Station Bag Side Flap-2 Close FB | DI42_Filling Station Bag Side Flap-2 Close FB | Reed Switch | [PLC]RIO01_DI[50]
43 | DI43 |  | RP:8:I.2 | _ | Filling Station Bag Present Sensor | DI43_Filling Station Bag Present Sensor | Photo Sensor | [PLC]RIO01_DI[51]
44 | DI44 |  | RP:8:I.3 | _ | Filling Station Bag Clamp Foot Switch | DI44_Filling Station Bag Clamp Foot Switch | Foot Switch | [PLC]RIO01_DI[52]
45 | DI45 |  | RP:8:I.4 | _ | Filling Station Filling Start/Stop PB | DI45_Filling Station Filling Start/Stop PB | 2 Hand Push Button | [PLC]RIO01_DI[53]
46 | DI46 |  | RP:8:I.5 | _ | Filling Station Conveyor Up FB | DI46_Filling Station Conveyor Up FB | Reed Switch | [PLC]RIO01_DI[54]
47 | DI47 |  | RP:8:I.6 | _ | Filling Station Conveyor Dn FB | DI47_Filling Station Conveyor Dn FB | Reed Switch | [PLC]RIO01_DI[55]
48 | DI48 |  | RP:8:I.7 | _ | Spare DI | DI48_Spare DI |  | [PLC]RIO01_DI[56]
49 | DI49 |  | RP:9:I.0 | _ | Sealing Station Bag Entry Sensor | DI49_Sealing Station Bag Entry Sensor | Photo Sensor
50 | DI50 |  | RP:9:I.1 | _ | Sealing Station Bag Exit Sensor | DI50_Sealing Station Bag Exit Sensor | Photo Sensor
51 | DI51 |  | RP:9:I.2 | _ | Sealing Station Band Sealer Machine Ready | DI51_Sealing Station Band Sealer Machine Ready | Contact
52 | DI52 |  | RP:9:I.3 | _ | Sealing Station Band Sealer Machine Running | DI52_Sealing Station Band Sealer Machine Running | Contact
53 | DI53 |  | RP:9:I.4 | _ | Sealing Station Band Sealer Machine Temperature OK | DI53_Sealing Station Band Sealer Machine Temperature OK | Contact
54 | DI54 |  | RP:9:I.5 | _ | Sealing Conveyor Start Foot Switch | DI54_Sealing Conveyor Start Foot Switch | Foot Switch
55 | DI55 |  | RP:9:I.6 | _ | Spare DI | DI55_Spare DI
56 | DI56 |  | RP:9:I.7 | _ | Stitching Station Cycle Start Foot Switch | DI56_Stitching Station Cycle Start Foot Switch | Foot Switch
57 | DI57 |  | RP:10:I.0 | _ | Stitching Station Bag Entry Sensor | DI57_Stitching Station Bag Entry Sensor | Photo Sensor
58 | DI58 |  | RP:10:I.1 | _ | Stitching Station Bag Exit Sensor | DI58_Stitching Station Bag Exit Sensor | Photo Sensor
59 | DI59 |  | RP:10:I.2 | _ | Stitching Station Thread Cutter Cylinder Fwd FB | DI59_Stitching Station Thread Cutter Cylinder Fwd FB | Reed Switch
60 | DI60 |  | RP:10:I.3 | _ | Stitching Station Thread Cutter Cylinder Rev FB | DI60_Stitching Station Thread Cutter Cylinder Rev FB | Reed Switch
61 | DI61 |  | RP:10:I.4 | _ | Stitching Station Thread breake Detection Sensor-1 | DI61_Stitching Station Thread breake Detection Sensor-1 | Thread Sensor
62 | DI62 |  | RP:10:I.5 | _ | Stitching Station Thread breake Detection Sensor-2 | DI62_Stitching Station Thread breake Detection Sensor-2 | Thread Sensor
63 | DI63 |  | RP:10:I.6 | _ | Stitching Station Stitching Start Sensor | DI63_Stitching Station Stitching Start Sensor | Photo Sensor
64 | DI64 |  | RP:10:I.7 | _ | Stitching Station Stitching StopSensor | DI64_Stitching Station Stitching StopSensor | Photo Sensor
65 | DI65 |  | RP:11:I.0 | _ | Tilting Station Bag Present Sensor | DI65_Tilting Station Bag Present Sensor | Photo Sensor
66 | DI66 |  | RP:11:I.1 | _ | Bag Flattner Station Bag Entry Sensor | DI66_Bag Flattner Station Bag Entry Sensor | Photo Sensor
67 | DI67 |  | RP:11:I.2 | _ | Bag Flattner Station Bag Exit Sensor | DI67_Bag Flattner Station Bag Exit Sensor | Photo Sensor
68 | DI68 |  | RP:11:I.3 | _ | Spare DI | DI68_Spare DI
69 | DI69 |  | RP:11:I.4 | _ | Spare DI | DI69_Spare DI
70 | DI70 |  | RP:11:I.5 | _ | Metal Detector Station Bag Entry Sensor | DI70_Metal Detector Station Bag Entry Sensor | Photo Sensor
71 | DI71 |  | RP:11:I.6 | _ | Metal Detector Station Bag Exit Sensor | DI71_Metal Detector Station Bag Exit Sensor | Photo Sensor
72 | DI72 |  | RP:11:I.7 | _ | Metal Detector FB | DI72_Metal Detector FB
73 | DI73 |  | RP:12:I.0 | _ | Rejection Station Bag Present Sensor | DI73_Rejection Station Bag Present Sensor | Photo Sensor
74 | DI74 |  | RP:12:I.1 | _ | Rejection Station Bag Entry Sensor | DI74_Rejection Station Bag Entry Sensor | Photo Sensor
75 | DI75 |  | RP:12:I.2 | _ | Rejection Station Bag Exit Sensor | DI75_Rejection Station Bag Exit Sensor | Photo Sensor
76 | DI76 |  | RP:12:I.3 | _ | Rejection Station Pusher Cyl Forward FB | DI76_Rejection Station Pusher Cyl Forward FB | Reed Switch
77 | DI77 |  | RP:12:I.4 | _ | Rejection Station Pusher Cyl Reverse FB | DI77_Rejection Station Pusher Cyl Reverse FB | Reed Switch
78 | DI78 |  | RP:12:I.5 | _ | Spare DI | DI78_Spare DI
79 | DI79 |  | RP:12:I.6 | _ | Packing Zone Dust Collector Level High | DI79_Packing Zone Dust Collector Level High | Level Sensor
80 | DI80 |  | RP:12:I.7 | _ | Dust Collector Discharge BFV Open FB | DI80_Dust Collector Discharge BFV Open FB | Valve FB
81 | DI81 |  | RP:13:I.0 | _ | Dust Collector Discharge BFV Open FB | DI81_Dust Collector Discharge BFV Open FB | Valve FB
82 | DI82 |  | RP:13:I.1 | _ | Spare DI | DI82_Spare DI
83 | DI83 |  | RP:13:I.2 | _ | Spare DI | DI83_Spare DI
84 | DI84 |  | RP:13:I.3 | _ | Spare DI | DI84_Spare DI
85 | DI85 |  | RP:13:I.4 | _ | Spare DI | DI85_Spare DI
86 | DI86 |  | RP:13:I.5 | _ | Spare DI | DI86_Spare DI
87 | DI87 |  | RP:13:I.6 | _ | Spare DI | DI87_Spare DI
88 | DI88 |  | RP:13:I.7 | _ | Spare DI | DI88_Spare DI
Sl No | Input Type | Location | Address |  | Input Description | Input Tags | Device | TAG | Sl No | Output Type | Location | Address | Output Description | Output Tags | Device | TAG
[5 empty] | ANALOG INPUT | Input Tags | [6 empty] | ANALOG OUTPUT
1 | AI01 |  | RP:19:I.Ch0 | _ | Coarse Vibro Level Sensor | AI01_Coarse Vibro Level Sensor
2 | AI02 |  | RP:19:I.Ch1 | _ | Fine Vibro Level Sensor | AI02_Fine Vibro Level Sensor
3 | AI03 |  | RP:19:I.Ch2 | _ | Dust Collector Pressure Transmitter | AI03_Dust Collector Pressure Transmitter
4 | AI04 |  | RP:19:I.Ch3 | _ | Dust Collector Pressure Transmitter | AI04_Dust Collector Pressure Transmitter
5 | AI05 |  | RP:20:I.Ch0 | _ | Spare AI | AI05_Spare AI
6 | AI06 |  | RP:20:I.Ch1 | _ | Spare AI | AI06_Spare AI

## Network
Project Network

## Drive
[5 empty] | 13 | 5 | 2 | 1 | 1 | 2
Chopper Motor-1 | CM001 | VFD | 3.7 | 3.7 | 0.75 | 1.5 | 3.7 | 5.5 | 7.5 | 22.5
Chopper Motor-2 | CM002 | VFD | 3.7 | 3.7
Anti-Static Coating Roller | ASCR001 | VFD | 0.75 | 0.5
Spreader Motor-2 | SM001 | VFD | 0.75 | 0.5
Feeders-1 (In Future Scope) | - | VFD | 0.75 | 0.18
Feeders-2 (In Future Scope) | - | VFD | 0.75 | 0.18
Feeders-3 (In Future Scope) | - | VFD | 0.75 | 0.37
Dryer Heating Zone Inlet Blower | DHIB01 | VFD | 22.5 | 22.5
Dryer Heating Zone Dust Collector | DHDC01 | VFD | 22.5 | 22.5
Dryer Cooling Zone Inlet Blower | DCIB01 | VFD | 5.5 | 5.5
Dryer Cooling Zone Dust Collector | DCDC01 | VFD | 7.5 | 7.5
Dryer Conveyor Motor | DCM | VFD | 1.5 | 1.1
Incliend Belt conveyor | IBC001 | VFD | 1.5 | 1.1
Material Storage Vibro-1 | MSV01 | VFD | 1.5 | 1.1
Material Storage Vibro-2 | MSV02 | VFD | 1.5 | 1.1
Bag Filling Conveyor | BFC01 | VFD | 0.75 | 0.75
Bag Sealing & Stiching Conveyor | BSSC01 | VFD | 0.75 | 0.75
Bag Stitching Motor | BSM01 | DOL | 0.75 | 0.75
Bag Tilting Conveyor | BTC01 | VFD | 0.75 | 0.75
Bag Flattening Bottom Conveyor | BFBC01 | VFD | 0.75 | 0.75
Bag Flattening Top Conveyor | BFTC01 | VFD | 0.75 | 0.75
Metal Detector Conveyor | MDC01 | VFD | 0.75 | 0.75
Bag Rejection Conveyor | BRC01 | VFD | 0.75 | 0.75
Bagging Zone Dust Collector | BDCB01 | DOL | 1.5 | 1.1